## Room
Take lots of pictures to refer to later
What is the water sources?
Well
Tank
Municipal
Where does the Water enter the room?
What is the fitting where the water enters the room? We want to understand how we will connect to it
Is there a shut off valve for raw water input or will one be needed? We want to be able to drain the Raw water tank
Will there need to be a barrel sand filter included in the system?
Where will the Drain be in the room?
What fitting will the drain have where it exits the room?
Is the floor relatively level, or find the low spot
What will it drain into?
Drywell
Septic System
Street or alley
Municipal Sanitary/Storm drain
The Drain water will have chlorine in it after shocking
What is the source of electrical power?
Municipal?
Generator?
Solar?
How does it come into the Room?
Do we need to install a box with a breaker?
If there is an outlet in the room already, use outlet checker to confirm it is wired correctly
Do they need to have a Ground Rod Present?
Will there be an outlet close to where the Board will be mounted or will we need to add one?
Will there be an outlet for the Bottling station heat gun or will we need to add one?
Make sure that the door into the room is large enough to allow the Rotoplas 300G/1100L Tank to fit through.
1.1 M at least since this is the Diameter of the tank
Think about best location for the Rinse station sink
With respect to the Drain
With respect to the board
With respect to where the Raw Water tank will be placed
With respect to where the Pure Water tank will be placed
Sketch out a proposed Room Layout, floor plan
Sketch out an elevation view to show the relative heights of components and define the stands that will be needed
To bottom of Board from floor
Raw Water Tank
Pure Water Tank
Barrel Sand filter if needed
Confirm that they will have the 4x8 foot sheet of plywood mounted prior to arrival of the Installation team
Confirm that it will be painted
Plan to use the Johnny design for the Rinse Station
Think about another raw water line that would go to a second room for the Dirty Bottle cleaning intake cleaning
This may entail a Tee after the Flow Guage and a Valve going to this location, so there is water pressure.
And Possibly another sink or basin ourside of the water room.
With a drain for this sink
How is the Lighting in the room?
How is the ventilation in the room, will we be able to have fans brought in during the installation?

## Sanitary_Spanish
OK as is
Room needs to be constructed
Needs improvement
OP agrees to try to comply
Bathroom (if there is one close)
Must be in good working order
* |  |  |  |  | Cannot be inside of the production area
Can be next to the production area
Door must not open directly into the production area
Note how far away the bathroom is from the entrance to the production
Needs to have a hand washing station with antibacterial liquid soap; bar soap is not acceptable
Disposable paper towels must be available; cloth towels are not acceptable
Need a sign that says "Wash Your Hands" with a graphic (should post same sign in water room)
Area to wash used bottles
Must be outside of the production area
Use of raw water to wash exterior dirt off is acceptable
Have a way to clean off boots or shoes prior to entering the production area
Have a way to drain this washing station
Production area (where the system is installed)
There should be a pedal or touch washbasin different from the one used to wash bottles and the bathroom
Solid construction, appropriate and in good condition
Must prevent insects, birds, rodents and other pests from entering or nesting
Must prevent pollutants like smoke and dust from entering and also allow good ventilation
Floor
Easy to clean and non-slip
Tile floor is preferred
Sanitary curve strips are required at wall to floor joint to avoid corners for insect nesting
Walls
Tile preferred and at least 1.5 to 2M high
Smooth plaster painted and without cracks is acceptable
Non-absorbent material
Paint with light colors
Easy to clean and wash
Must NOT be wood
Roof/Ceiling
Roof without openings, well-sealed to keep out trash, dust, mice and insects
In good condition, with smooth surface
Outer roofing material must NOT be wood
Looks like an interior drop ceiling with acoustic tiles is okay
Doors
Solid closing doors should also have a screen/mesh door so solid door can be open for ventilation but keep out insects
Doors should open outward
Non-absorbent material
Screen doors
Windows
Windows open and close and have screens/mesh to keep out insects
Screen/mesh also to keep glass from coming into the production area if window breaks
Drains - should have at least 3 drains
System drain (can share with rinse station)
Drain for bottle cleaning area
Floor drain
Pipe should be at least 2.5 inches in diameter
Drains must have covers, screens or be sealed to prevent insects and rodents from entering
Lighting
Can be natural or artificial
Lamps must be covered to protect the bulb and contain glass particles if bulb bursts
This protection must be plastic
No hanging wires in the production area
Power
110 Volts, #8 gauge wire to fuse box
Need to have a well-connected grounding rod
Tanks
Tanks should be located inside the production area to protect from contamination, rain and sun
System piping
Pure water pipes have green labels
Arrows showing direction of flow
Area for disinfection, rinsing, filling and sealing bottles
Usually inside of production area
Follow LWW bottle washing, filling and sealing procedures
Storage area
Area for storage of empty and filled bottles
Area for storage of caps, seals and other supplies
Needs to be clean and prevent risk of contamination for filled bottles
Could be in production area
Delivery area
Looks like it can be a window into the production area
*Must be ready prior to installation of system